E

Honeywell

V4-ABFW-EPN16

ACTUATED WAFER TYPE BUTTERFLY VALVES

PRODUCT SPECIFICATION SHEET

FEATURES

•

•

•

•

•

•

•

•

•

•

Cast Iron Wafer Body

Centric butterfly valve with elastomer liner

Wide DN-range (DN 50 … DN600)

For On/Off or Modulating Control

Robust actuators in epoxy coated aluminum

Manual override non-clutch design. Manual operation can be

operated without any lever, clutch or brake upon power voltage.

Irreversible worm gear

Visual mechanical position indicator for accurate visual reference

of valve position

Anti-condensation heater and 2 aux. limit switches on standard

model

Enclosure IP67

SPECIFICATIONS

Valve

Sizes

Nominal pressure

Tightness

Temperature range

Body

Shaft

Disc

Liner

DN50 – DN600(Wafer Type)

PN16

Bubble tight

0-10 ~ 120 C Maximum

Cast Iron, BS EN1561 EN-JL1030

Stainless Steel, 970 416S21

Ductile Iron with epoxy coating

EPDM

GENERAL

The V4 Actuated Wafer Type Butterfly Valves are

suitable for heating and cooling applications. They can

also be employed for industrial applications, general

services and water treatment.

The V4 series is equipped with standard On/Off or

modulating (4~20mA, 1~5V, or 0(2)~10V select by

DIP-switch) control quarter-turn electric actuator.

Actuator

Motor Voltage

Current, Running time

Travel Angle

Input (Modulating)

Enclosure

Ambient Temperature

Indicator

Manual Override

Worm Gear

Mechanical Stops

Space heater

Material

External Coating

Stall Protection

230VAC, 50 / 60 Hz

See table (1)

oo90 ± 5

4~20mA, 1~5V, or 0(2)~10V select by DIP-

switch

IP67 Watertight

-5 °C to +60 °C

Continuous Position Indicator

Non-clutch design

Permanently lubricated and self locking

External Adjustable Limit stops

15W 230V Anti-condensation

Steel. Aluminium Alloy, Al Bronze

Anodized and dry powder epoxy

Built-in thermal protection

Cut off at 125 ± 5 °C

Reset at 95 ± 5 °C

V4-ABFW-EPN16 ACTUATED BUTTERFLY VALVE

Table (1) Control Type and Valve Size Data

The below table is based on differential pressure of 10 bar.

Valve

Size

DN50

DN65

DN80

DN100

DN125

DN150

DN200

DN250

DN300

DN350

DN400

DN450

DN500

DN600

On/Off

Model No.

V4-ABFW-EPN16-050-03

V4-ABFW-EPN16-065-03

V4-ABFW-EPN16-080-03

V4-ABFW-EPN16-100-03

V4-ABFW-EPN16-125-03

V4-ABFW-EPN16-150-03

V4-ABFW-EPN16-200-03

V4-ABFW-EPN16-250-03

V4-ABFW-EPN16-300-03

V4-ABFW-EPN16-350-03

V4-ABFW-EPN16-400-03

V4-ABFW-EPN16-450-03

V4-ABFW-EPN16-500-03

V4-ABFW-EPN16-600-03

Actuator

Type

OM-1

OM-1

OM-2

OM-2

OM-2

OM-3

OM-3

OM-4

OM-5

OM-7

OM-8

OM-8

OM-9

OM-11

Modulating

Model No.

V4-ABFW-EPN16-050-04

V4-ABFW-EPN16-065-04

V4-ABFW-EPN16-080-04

V4-ABFW-EPN16-100-04

V4-ABFW-EPN16-125-04

V4-ABFW-EPN16-150-04

V4-ABFW-EPN16-200-04

V4-ABFW-EPN16-250-04

V4-ABFW-EPN16-300-04

V4-ABFW-EPN16-350-04

V4-ABFW-EPN16-400-04

V4-ABFW-EPN16-450-04

V4-ABFW-EPN16-500-04

V4-ABFW-EPN16-600-04

Max Op Time

ActuatorPower

Torque sec/90°

Type(Watts)

(Nm) at 60Hz

OM-P1

OM-P1

OM-P2

OM-P2

OM-P2

OM-P3

OM-P3

OM-P4

OM-P5

OM-P7

OM-P8

OM-P8

OM-P9

OM-P11

35

35

35

90

90

150

150

400

500

1000

1500

1500

2000

3000

12

12

12

15

15

22

22

22

22

46

46

46

58

58

10

10

10

40

40

40

40

120

120

180

220

220

220

250

Manual

Override

Lever

Lever

Lever

Hand-wheel

Hand-wheel

Hand-wheel

Hand-wheel

Hand-wheel

Hand-wheel

Hand-wheel

Hand-wheel

Hand-wheel

Hand-wheel

Hand-wheel

Kvs

(m3/h)

100

170

281

619

884

1366

2713

4819

7136

10485

14007

18560

23860

36900

Weight

Kg

13.4

14.4

14.6

16.6

20.1

25.0

29.9

43.4

55.8

89.0

145.0

165.0

184.0

241.0

Figure (1) Product Identification System

The labeling system for Honeywell butterfly valves is as follows:

V4 – ABFW – EP16 – 050 – 03 -

ABFW – Wafer body

ABFL – Lug body

Valve Size in mm

Disc Material

– Ductile iron

1 – Stainless steel

2 - AluBronze

Control Type

03 – On/Off control

04 – Modulating control

V4-ABFW-EPN16 ACTUATED BUTTERFLY VALVE

Table (2) Valve Dimensions and Weight

Size

A

B

C1

D

E

F

KxK Weight

(Kg)

4.5

5.4

5.6

7.6

10.1

12.0

16.9

26.4

37.8

67

110

127

160

185

Top Plate Date

PCD HOLE N-Dia.

DN50

DN65

DN80

DN100

DN125

DN150

DN200

DN250

DN300

DN350

DN400

DN450

DN500

DN600

140

152

159

70

76

88

105 41

117 44

130 44

90

90

90

90

90

90

30 11x11

30 11x11

30 11x11

30 14x14

30 14x14

30 17x17

70

70

70

70

70

70

102

102

102

125

140

140

140

165

4 - Ø9

4 - Ø9

4 - Ø9

4 - Ø9

4 - Ø9

4 - Ø9

4 - Ø11

4 - Ø11

4 - Ø11

4 - Ø14

4 - Ø18

4 - Ø18

4 - Ø18

4 – Ø22

178 102 162 51

191 119 187 54

203 133 216 54

241 170 271 64 125 45 17x17

273 210 330 64 125 45 22x22

311 238 376 76 125 45 22x22

368 267 436 80 150 45 22x22

400 309 488 90 175 45 27X27

422 318 535 109 175 45 27X27

480 350 585 127 175 45 36X36

562 410 685 154 210 45 36X36

Table (3) Hydraulic Characteristics

The below table shows the Kv – values at different opening angles:

Nominal Size

10o

DN50

DN65

DN80

DN100

DN125

DN150

DN200

DN250

DN300

DN350

DN400

DN450

DN500

DN600

0.05

0.09

0.17

0.26

0.43

0.69

1.70

2.60

3.50

5.1

6.8

9.4

11.9

18.8

Kv – value at Disk Opening Angle

20o

2.60

5.20

7.80

15

25

39

77

131

202

289

397

526

676

1044

30o

6.10

10

16

31

53

82

163

277

428

611

840

1113

1431

2211

40o

13

22

34

68

115

177

353

600

927

1324

1821

2412

3101

4791

50o

23

39

61

120

205

317

629

1070

1653

2360

3245

4297

5526

8538

60o

38

65

100

199

339

523

1040

1771

2735

3904

53639

7111

9144

14126

70o

61

103

158

315

536

829

1646

2803

4329

6179

8497

11255

14471

22356

80o

91

154

238

472

804

1243

2469

4205

6494

9268

12746

16882

21706

33535

90o

100

170

261

519

884

1366

2713

4619

7136

10185

14007

18551

23853

36851

V4-ABFW-EPN16 ACTUATED BUTTERFLY VALVE

Table (4a) Actuator Dimensions

(OM-1)

Model A B CDEFGHIJ

No.

OM-1 108 8 45° 155 15 36 m5 4 m6 6

LM

max

50 14 19

K

N

Flange

Type

1 ½ PT F03/F05

S

Table (4b) Actuator Dimensions

(OM-2 to OM-3, OM-4 to OM-6)

GHIM

Max

OM-2 to OM-3 200 300 200 255 30 125 22 70 m8 4

OM-4 to OM-6 300 380 234 315 40 195 35 102 m10 4

Model No.

A

B

C

D

E

F

N

2

2

Flange

Type

½ PT F07

½ PT F10

S

Option: (1) L = 11, M = 15

(2) L = 9, M = 12

With modulating card, D = 185

Table (4c) Actuator Dimensions

(OM-7 to OM-8)

Model ABCDEFGHIJKLM N S Flange

No.maxType

OM-7 to 450 340 234 420 60 295 140 45° m16 4 180 10 35 2 ½F14

OM-8PT

Table (4d) Actuator Dimensions

(OM-9 to OM-12)

Model A B C D E F G HIJ

No.

OM-9 to 470 350 260 590 100 395 45° 12 m20 4

OM-12

K

L

M

P

N

S Flange

Type

½ F16/F14

PT

75 165 221 360 2

Note:

without torque switch A = 385

V4-ABFW-EPN16 ACTUATED BUTTERFLY VALVE

INSTALLATION

WARNING!

Remove power before the cover is

dismantled!

The actuator must be handled with the

utmost care when the cover is removed

and the power connected!

ELECTRIC WIRING

Note:

Electric wiring must be carried out by

qualified personnel only!

Wiring diagram is also shown on the label of

top cover.

Loosen the screws on the cover and lift it off.

Check the voltage marked on the actuator label.

MOUNTING ON VALVE

Operate the valve manually to fully open or fully closed

position before the actuator is mounted.

Operate the actuator and valve stem to fully open or

fully closed position.

Check that the actuator and valve stem are in correct

position. Please note, valve and actuator must be in

the same mode (fully open/fully closed) prior to the

assembly.

Mount the actuator on the valve and check that the

actuator and valve stems are centered and aligned.

Operate the valve manually with the aid of the actuator

hand-wheel and check that the valve moves with

normal resistance.

Check that all screws are correctly tightened.

Connect according to the enclosed wiring diagram or if

the actuator is of standard design, according to the wiring

diagram below. The wiring diagram is drawn in unaffected

position (the valve in the intermediate position).

Test run the actuator from intermediate position checking

that the actuator turns in the correct direction.

Test run the actuator and check that the limit switches

work correctly.

Check that the cable entries and possible blind plug are

sealed.

Mount the cover.

V4-ABFW-EPN16 ACTUATED BUTTERFLY VALVE

WIRING DIAGRAM FOR MODULATING

WIRING DIAGRAM FOR ON/OFF

V4-ABFW-EPN16 ACTUATED BUTTERFLY VALVE

FUNCTION SETTING

Note:

Turn the power off before changing the following

setting.

S1~S8: Function setting by DIP switches

S1, S2: DIP switches for input signal select

“4~20mA” set 1-ON / 2-OFF.

“1~5V” set 1-OFF / 2-OFF.

“2~10V” set 1-OFF / 2-ON.

S3, S4, S5: DIP switches for feedback signal select

“2~10V” set 3-ON / 4-OFF / 5-ON.

“4~20mA” set 3-OFF / 4-ON / 5-OFF.

S6: DIP switch for direct/reverse action

Valve is fully-open when the input signal is 4mA, 2V or 1V

and valve is fully-closed when the input signal is 20mA, 10V

or 5V, set 6-ON.

Valve is fully-closed when the input signal is 4mA, 2V or 1V

and valve is fully-open when the input signal is 20mA, 10V or

5V, set 6-OFF.

S7, S8: DIP switches for valve position when input signal fails

“valve fully-closed” set 7-OFF / 8-ON.

“valve fully-open” set 7-ON / 8-OFF.

“valve stops” set 7-ON / 8-ON.

SW1~0 (10 steps): Sensitivity adjustable switch

When switch to “1”, the 0~90 degree can be divided up to

around 80 times movement.

When switch to “0”, the 0~90 degree can be divided up to

around 17 times movement.

The sensitivity decreases 7 times movement by sectors from

SW1 to SW2, SW2 to SW3, SW3 to SW4 and so on.

V4-ABFW-EPN16 ACTUATED BUTTERFLY VALVE

TROUBLE SHOOTING

Conditions

Motor does not operate

Possibilities

1. Is the supplied power and voltage

correct?

2. Any blisters on the capacitor?

3. Are the gear train free?

1. Is the power supply short circuited?

2. Any foreign objects in flow stream?

1. Loose/Misalign cam?

2. Bent valve stem?

3. Mechanical stop adjustment incorrect?

1. Gear worn out?

2. Sleeve adapter worn out or broken?

3. Broken valve stem or actuator

transmission shaft?

Controlling circuit connects in tandem or

parallel.

1. Is the voltage correct?

2. Is valve too tight to operate?

3. High duty working frequency?

4. Is motor stem bearing or blinding?

Simultaneous input power on/off.

Motor brake spring fatigued or Teflon

worn?

Solution

1. Check by meter.

2. If so, replace.

3. Remove motor and check.

1. Check wiring.

2. Check for obstructions.

1. Adjust/Tighten using spanner.

2. Replace valve stem.

3. Check position of stops.

1. Replace gear.

2. Replace sleeve adapter.

3. Replace valve stem or actuator

transmission shaft.

Refer to the wiring diagram.

1. Check by meter.

2. Replace valve.

3. Check duty cycle.

4. Replace the blinding parts.

Check if the selectable switch is normal.

Replace spring or Teflon.

Motor stops running

Unable to fully open/close

Valve stops operating when motor is

running.

Abnormal control for operating two or

more actuators simultaneously.

Motor overheats

Occasional on/off actuator failure.

Vibration when valve is closed.